| JOB HAZARD ANALYSIS (JHA) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date submitted | Xx/xx/xxxx |  | Estimated start date | Xx/xx/xxxx |  |
| Company Performing Work |  |  |  |  |  |
| Prime Controls |  |  |  |  |  |
| Description of work |  |  |  |  |  |
| MDN AHU/ERU Pressure Switch Mapping |  |  |  |  |  |
| Project Name: MDN3A |  |  |  |  |  |
| Location of work: HUB Control Room, FSA Yard |  |  |  |  |  |
| Analysis written by: Johnny Blevins |  | Title: AS |  |  | Contact # 940-229-2486 |
| Analysis Reviewed by: Chris Hughes |  | Title: Assistant Project Manger |  |  | Contact # 469-410-2670 |
| Analysis Approve by: |  | Title: |  |  | Contact # |
| Permits Required |  |  |  |  |  |
| Orientation, Training Required or Prerequisites |  |  |  |  |  |
| Tools & Equipment |  |  |  |  |  |

N/A

PPE Required

Minimum: Hard Hat (Type 2/Type 1 with EN12492 rating), Safety eyewear (Z87.1), ANSI High Viz Class II outerwear/vest, ANSI 4 cut resistant gloves or task specific.

| Sequence of Basic Job Steps | Identified Safety & Environmental Hazards | Precautionary Actions and Control Procedures to be Taken |
| --- | --- | --- |
| Step 1: Contact the Client POC before starting work. | Employees not having proper training (See training required listed above) | Work must not start until POC is contacted. Supervisor and safety to have employees trained prior to work starting. |
| Step 2: Check in worknote daily (972) 775-5050. | N/A | Work must not start until the work note is approved every morning. |
| Step 3: Contact JE Dunn Super with JE Dunn Kullen Neyens (515) 991-0040. | N/A | Work must not start until JE Dunn super is contacted. |
| Step 4: Check out the Engineering Workstation for system access. | N/A | N/A |
| Step 5: **The following steps are to edit the existing Kepware tag database. Unused tags will be deleted, and some tags will be repurposed to reflect the new design change. Using Remote Desktop, remote into the BMS-MDN3A-FTS1A server at IP 172.21.30.230. On the server, open KEPServerEX 6 Configuration. - Take a current backup of the file by saving it as “BMS-MDN3A-FST1x_yyyymmdd_AsFound.opf” To avoid working in the backup file, do another save as and name the file “BMS-MDN3A-FTS1x_yyyymmdd_AsLeft.opf”. | N/A | Proceed with caution, avoid distractions while working. Saving an “AsFound” file prior to proceeding with changes is CRITICAL in case we need to revert back to the original running code. |
| Step 6: In the running Kepware configuration file, expand the “FSA_MAS” channel and complete steps 7-10 below: | N/A | Proceed with caution, avoid distractions while working. |
| Step 7: Select the device named “AHU_D01” to see the list of associated tag groups. For the tag at BinaryInput.17.PresentValue, make the following changes: - Tag Name changes to: B3A_SVR_AHU1 _PS_ALM Description changes to: SVR AHU1 PRESSURE SWITCH ACTIVE | N/A | See previous step. |
| Step 8: Select the device named “AHU_D02” to see the list of associated tag groups. For the tag at BinaryInput.17.PresentValue, make the following changes: - Tag Name changes to: B3A_SVR_AHU2_ PS_ALM Description changes to: SVR AHU2 PRESSURE SWITCH ACTIVE | N/A | See previous step. |
| Step 9: Expand the device named “ERU_F01” to see the list of associated tag groups. Make the following changes to the list of tags: - Delete the tag group B3A_FSA_ERU1_EXH_FAN_PSH715B_ALM - Delete the tag group B3A_FSA_ERU1_EXH_FAN_PSL715A_ALM - Delete the tag group B3A_FSA_ERU1_SPLY_FAN_DPSW704_STS - Delete the tag group B3A_FSA_ERU1_SPLY_FAN_PSH706B_ALM - For tag group B3A_FSA_ERU1_SPLY_FAN_PSL706A_ALM (BinaryInput.17.PresentValue), make the following changes: - Tag name changes to: B3A_FSA_ERU1_PS_ALM Description changes to: ERU PRESSURE SWITCH ACTIVE | N/A | See previous step. |
| Step 10: If needed, reinitialize Kepware for the changes to take effect. **Note: Coordinate closely with the operational control room before reinitializing Kepware, as visibility may be temporarily lost. | N/A | See previous step. |
| Step 11: Using Remote Desktop, remote into the BMS-MDN3A-FTS1B server at IP 172.21.30.231. On the server, open KEPServerEX 6 Configuration. - Take a current backup of the file by saving it as “BMS-MDN3A-FST1x_yyyymmdd_AsFound.opf” To avoid working in the backup file, do another save as and name the file “BMS-MDN3A-FTS1x_yyyymmdd_AsLeft.opf”. | N/A | See previous step. |
| Step 12: Repeat steps 6-10 above on the secondary server. Before proceeding, take the backup files from each server and save them on the development server desktop to be passed by ops. | N/A | See previous step. |
| Step 13: Remote into the FactoryTalk Development Server and open FactoryTalk View Studio. Before proceeding, take a backup of the currently running applications by clicking Tools>Application Manager>Create A Backup. | N/A | See previous step. |
| Step 14: **The following steps are to edit the existing FactoryTalk HMI tags. Unused tags will be deleted, and new tags will be created to reflect the new design change. In the FactoryTalk View Studio Explorer pane, browse to the building 3A HMI tags to complete steps 15 through 17. | N/A | See previous step. |
| Step 15: SVR_AHU1: - Delete the HMI tag FSA_MAS\B3A_SVR_AHU1_SPLY_FAN_PSH506B_ALM - Delete the HMI tag FSA_MAS\B3A_SVR_AHU1_SPLY_FAN_PSL506A_ALM - Create a new HMI tag named FSA_MAS\B3A_SVR_AHU1_PS_ALM - Tag Description: SVR AHU1 PRESSURE SWITCH ACTIVE Address: Address the tag to the Kepware tag modified in step 7. | N/A | See previous step. |
| Step 16: SVR_AHU2: - Delete the HMI tag FSA_MAS\B3A_SVR_AHU2_SPLY_FAN_PSH506B_ALM - Delete the HMI tag FSA_MAS\B3A_SVR_AHU2_SPLY_FAN_PSL506A_ALM - Create a new HMI tag named FSA_MAS\B3A_SVR_AHU2_PS_ALM - Tag Description: SVR AHU2 PRESSURE SWITCH ACTIVE Address: Address the tag to the Kepware tag modified in step 8. | N/A | See previous step. |
| Step 17: FSA_ERU1: - Delete the HMI tag FSA_MAS\B3A_FSA_ERU1_EXH_FAN_PSH715B_ALM - Delete the HMI tag FSA_MAS\B3A_FSA_ERU1_EXH_FAN_PSL715A_ALM - Delete the HMI tag FSA_MAS\B3A_FSA_ERU1_SPACE_DPRS710 - Delete the HMI tag FSA_MAS\B3A_FSA_ERU1_SPLY_FAN_PSH706B_ALM - Delete the HMI tag FSA_MAS\B3A_FSA_ERU1_SPLY_FAN_PSL706A_ALM - Create a new HMI tag named FSA_MAS\B3A_FSA_ERU1_PS_ALM - Tag Description: FSA ERU1 PRESSURE SWITCH ACTIVE - Address: Address the tag to the Kepware tag modified in step 9. | N/A | See previous step. |
| Step 18: **The following steps are to modify the PLC logic will involve making edits to live code. We will remove or “NOP” unused I/O mapping due to the removal of the HMI tags above. We will also add new I/O mapping (STD_DI add-on instructions) for the newly created HMI tags, and insert their alarm points into the AHU/ERU startup and shutdown logic. Using the VM installed on the engineering workstation, open LogixDesigner and connect to the running FSA_MAS PLC using address 172.21.31.70. Upload from the PLC by creating a new file called “FSA_MAS_AsFound_yyyymmdd” and save it on the desktop of the VM. Next “save as” the file as “FSA_MAS_AsLeft_yyyymmdd” and continue working in this file. | N/A | See previous step. |
| Step 19: In the controller organizer pane, expand the “Main Task”, then expand the “A2_IO_Mapping” program. Finally, open the “Digital Inputs” routine. Make the following edits in this routine: - Rung 4 (AHU1_SPLY_FAN_PSH506B_ALM): Add “NOP” instruction. - Rung 5 (AHU1_SPLY_FAN_PSL506A_ALM): Add “NOP” instruction. - Rung 10 (AHU2_SPLY_FAN_PSH506B_ALM): Add “NOP” instruction. - Rung 11 (AHU2_SPLY_FAN_PSL506A_ALM): Add “NOP” instruction. - Rung 16 (ERU1_SPLY_FAN_PSH706B_ALM): Add “NOP” instruction. - Rung 18 (ERU1_EXH_FAN_PSH715B_ALM): Add “NOP” instruction. - Rung 19 (ERU1_SPLY_FAN_PSL706A_ALM): Add “NOP” instruction. - Rung 20 (ERU1_EXH_FAN_PSL715A_ALM): Add “NOP” instruction. Next, add new rungs, instructions, and controller tags to map in the newly created HMI tags created in steps 15, 16, and 17. Add them in logical order with the other tags for each unit. - Add a new rung and STD_DI add-on instruction and create a new controller tag for B3A_SVR_AHU1_PS_ALM. - Add a new rung and STD_DI add-on instruction and create a new controller tag for B3A_SVR_AHU2_PS_ALM. - Add a new rung and STD_DI add-on instruction and create a new controller tag for B3A_FSA_ERU1_PS_ALM. Adjust the configuration parameters for each of the new AOIs as needed during troubleshooting and testing. | N/A | See previous step. |
| Step 20: In the controller organizer pane, expand the “Main Task”, then expand the “A4_Process_Control” program. Finally, open the “AHU_Control” routine. Make the following edits in this routine: - In rung 9 (inhibit alarms during AHU1 startup): - Add an “NOP” to the “B3A_SVR_AHU1_SPLY_FAN_PSH506B_ALM.Config_AlarmDisab” OTL. - Add an “NOP” to the “B3A_SVR_AHU1_SPLY_FAN_PSL506A_ALM.Config_AlarmDisab” OTL. - Add a new OTL addressed “B3A_SVR_AHU1_PS_ALM.Config_AlarmDisab”. - In rung 10 (enable alarms once AHU1 has started): - Add an “NOP” to the “B3A_SVR_AHU1_SPLY_FAN_PSH506B_ALM.Config_AlarmDisab” OTU. - Add an “NOP” to the “B3A_SVR_AHU1_SPLY_FAN_PSL506A_ALM.Config_AlarmDisab” OTU. - Add a new OTU addressed “B3A_SVR_AHU1_PS_ALM.Config_AlarmDisab”. - In rung 16 (inhibit alarms during AHU2 startup): - Add an “NOP” to the “B3A_SVR_AHU2_SPLY_FAN_PSH506B_ALM.Config_AlarmDisab” OTL. - Add an “NOP” to the “B3A_SVR_AHU2_SPLY_FAN_PSL506A_ALM.Config_AlarmDisab” OTL. - Add a new OTL addressed “B3A_SVR_AHU2_PS_ALM.Config_AlarmDisab”. - In rung 17 (enable alarms once AHU2 has started): - Add an “NOP” to the “B3A_SVR_AHU2_SPLY_FAN_PSH506B_ALM.Config_AlarmDisab” OTU. - Add an “NOP” to the “B3A_SVR_AHU2_SPLY_FAN_PSL506A_ALM.Config_AlarmDisab” OTU. - Add a new OTU addressed “B3A_SVR_AHU2_PS_ALM.Config_AlarmDisab”. - In rung 23 (inhibit alarms during ERU1 startup): - Add an “NOP” to the “B3A_FSA_ERU1_SPLY_FAN_PSH706B_ALM.Config_AlarmDisab” OTL. - Add an “NOP” to the “B3A_FSA_ERU1_SPLY_FAN_PSL706A_ALM.Config_AlarmDisab” OTL. - Add an “NOP” to the “B3A_FSA_ERU1_EXH_FAN_PSH715B_ALM.Config_AlarmDisab” OTL. - Add an “NOP” to the “B3A_FSA_ERU1_EXH_FAN_PSH715A_ALM.Config_AlarmDisab” OTL. - Add a new OTL addressed “B3A_FSA_ERU1_PS_ALM.Config_AlarmDisab”. - In rung 24 (enable alarms once ERU1 has started): - Add an “NOP” to the “B3A_FSA_ERU1_SPLY_FAN_PSH706B_ALM.Config_AlarmDisab” OTU. - Add an “NOP” to the “B3A_FSA_ERU1_SPLY_FAN_PSL706A_ALM.Config_AlarmDisab” OTU. - Add an “NOP” to the “B3A_FSA_ERU1_EXH_FAN_PSH715B_ALM.Config_AlarmDisab” OTU. - Add an “NOP” to the “B3A_FSA_ERU1_EXH_FAN_PSH715A_ALM.Config_AlarmDisab” OTU. Add a new OTU addressed “B3A_FSA_ERU1_PS_ALM.Config_AlarmDisab”. | N/A | See previous step. |
| Step 21: Save the file as “FSA_MAS_AsLeft_yyyymmdd” on the desktop of the VM. Remote into the development server and save the as-left file on the desktop. Request Ops to transfer the file via email to save offline. | N/A | See previous step. |
| Step 22: ** The following steps are required to modify the FactoryTalk alarms for the newly added tags. In the FactoryTalk View Studio Explorer pane, browse to the Building 3A alarms to complete steps 23 through 25. | N/A | See previous step. |
| Step 23: SVR_AHU1: - Delete the alarm B3A_SVR_AHU1_SPLY_FAN_PSH506B_ALM - Delete the alarm B3A_SVR_AHU1_SPLY_FAN_PSL506A_ALM - Create a new alarm named B3A_SVR_AHU1_PS_ALM - Message: “AHU1 PRESSURE SWITCH ACTIVE” Input Tag: /BLDG3A/BLDG3A_DATA::[FSA_MAS]B3A_SVR_AHU1_PS_ALM.Alarm | N/A | See previous step. |
| Step 24: SVR_AHU2: - Delete the alarm B3A_SVR_AHU2_SPLY_FAN_PSH506B_ALM - Delete the alarm B3A_SVR_AHU2_SPLY_FAN_PSL506A_ALM - Create a new alarm named B3A_SVR_AHU2_PS_ALM - Message: “AHU2 PRESSURE SWITCH ACTIVE” Input Tag: /BLDG3A/BLDG3A_DATA::[FSA_MAS]B3A_SVR_AHU2_PS_ALM.Alarm | N/A | See previous step. |
| Step 25: FSA_ERU1: - Delete the alarm B3A_FSA_ERU1_EXH_FAN_PSH715B_ALM - Delete the alarm B3A_FSA_ERU1_EXH_FAN_PSL715A_ALM - Delete the alarm B3A_FSA_ERU1_SPLY_FAN_PSH706B_ALM - Delete the alarm B3A_FSA_ERU1_SPLY_FAN_PSL706A_ALM - Create a new alarm named B3A_FSA_ERU1_PS_ALM - Message: “ERU PRESSURE SWITCH ACTIVE” Input Tag: /BLDG3A/BLDG3A_DATA::[FSA_MAS]B3A_FSA_ERU1_PS_ALM.Alarm | N/A | See previous step. |
| Step 26: **The following steps are to edit the graphical displays for the AHUs and ERUs. We will be combining the multiple pressure switch indicators for each unit into a single pressure switch indicator. In the FactoryTalk View Studio Explorer pane, browse to the displays for building 3A to complete steps 27 through 29. | N/A | See previous step. |
| Step 27: Open the display named “dc_ahu_d01_daikin”. Delete the indicators for pressure switches “PSL-506A” and “PSH-506B”. Create a new pressure switch indicator addressed to the new HMI tag “FSA_MAS\B3A_SVR_AHU1_PS_ALM” created in step 15 above. Name the indicator “Pressure Switch”. Save the display. | N/A | See previous step. |
| Step 28: Open the display named “dc_ahu_d02_daikin”. Delete the indicators for pressure switches “PSL-506A” and “PSH-506B”. Create a new pressure switch indicator addressed to the new HMI tag “FSA_MAS\B3A_SVR_AHU2_PS_ALM” created in step 16 above. Name the indicator “Pressure Switch”. Save the display. | N/A | See previous step. |
| Step 29: Open the display named “fsa_eru1_daikin”. Delete the indicators for pressure switches for “PSH-715B”, “PSL-715A”, “PSL-706A”, and “PSH-706A”. Create a new pressure switch indicator addressed to the new HMI tag “FSA_MAS\B3A_SVR_ERU1_PS_ALM” created in step 17 above. Name the indicator “Pressure Switch”. Save the display. | N/A | See previous step. |
| Step 30: **The following steps are to test the changes. We will physically manipulate each of the pressure switches in the units to ensure the edited programming is working correctly. **Work closely with the operational control room when manipulating units and causing alarms. | N/A | See previous step. |
| Step 31: For AHU1 - While the unit is running, stop the unit from the HMI. - With the unit shut down, start the unit from the HMI to ensure the pressure switch alarms are inhibited during startup. - Disconnect the supply fan high pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. Disconnect the supply fan low suction pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. | Electric shock. | Site-approved PPE. |
| Step 32: For AHU2 - While the unit is running, stop the unit from the HMI. - With the unit shut down, start the unit from the HMI to ensure the pressure switch alarms are inhibited during startup. - Disconnect the supply fan high pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. Disconnect the supply fan low suction pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. | Electric shock. | Site-approved PPE. |
| Step 33: For ERU1 - While the unit is running, stop the unit from the HMI. - With the unit shut down, start the unit from the HMI to ensure the pressure switch alarms are inhibited during startup. - Disconnect the supply fan high pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. - Disconnect the supply fan low suction pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. - Disconnect the exhaust fan high pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. Disconnect the exhaust fan low suction pressure switch and ensure the HMI indicator turns red. Wait 30 seconds to see the alarm. Reconnect the pressure switch. | Electric shock. | Site-approved PPE. |
| Step 34: During testing, troubleshoot as necessary. | N/A | N/A |
| Step 35: **Log out of all servers when work is complete. | N/A | N/A |
| Step 36: Contact the Client POC when work is complete. | N/A | N/A |
| Step 37: Check out worknote daily (972) 775-5050. | N/A | N/A |
| Step 38: Contact JE Dunn Super with JE Dunn Kullen Neyens (515) 991-0040. | N/A | N/A |